## Slide 1
Manhattan Commercial Office Building
$5 Million HVAC Modernization
Capital Expenditure & ROI Feasibility Study
Independent, hypothetical student project. No actual building investment or client engagement.
1 / 7
Mohamed Saffiddine
CUNY City Tech
Mechanical Engineering Technology student
Hypothetical Manhattan office: 500,000 ft²
Assumed cooling capacity: 1,200 tons
Objective: evaluate whether HVAC savings justify the required
capital investment over a 10-year period.
Notes: Suggested timing: 45 seconds I developed this independent project to connect mechanical engineering with capital investment analysis. I used a hypothetical 500,000-square-foot Manhattan office building with two assumed 600-ton chillers. I compared keeping the existing system, fully modernizing it, and making a smaller partial upgrade. My question was whether the modeled energy and operating savings justify the capital required over ten years. I used Excel to connect equipment performance and load assumptions to after-tax cash flows. The project uses documented sources and explicit estimates. It does not represent measured building performance, contractor bids, or an approved investment. Source notes (not part of spoken script): Manhattan_HVAC_CapEx_Final_Validated(1).xlsx, Assumptions!E9:E10 and E26. Step 5 executive summary, page 1, including author name and university. Study period: Year 0, 31 Dec 2026; Years 1–10, 2027–2036.

## Slide 2
Existing HVAC system
Conceptual adaptation of the Step 4 schematic. Hypothetical system, not a building design.
2 / 7
Building automation system (BAS): schedules, chiller staging, resets and drive commands
Cooling tower
and fans
Water-cooled chiller bank
Chiller 1
600 tons
Chiller 2
600 tons
Separate water circuits
Air-handling unit
Coil
SF
Office spaces
Warm CW
P
CW pump group
Cooled CW
P
CHW pumps
Supply CHW
Return CHW
Supply air
RF
Return air
Heat to outdoor air
Chilled water (CHW)
Condenser water (CW)
Airflow
BAS signals
Modeled baseline HVAC electricity: 3,043,500 kWh/year
Part-load efficiency, equipment condition and control schedules motivate the upgrade analysis.
Notes: Suggested timing: 60 seconds The chilled-water loop carries cooling from the evaporator sides of the chillers to the air-handling coil. A separate condenser-water loop carries rejected heat from the chillers to the cooling tower. The water loops do not mix. Supply fans move air through the coil to the offices, and return fans bring air back. The automation system controls schedules, staging and operating setpoints. This is a simplified adaptation of my report schematic. The pump symbols represent groups, not equipment counts. The workbook uses one combined pump-power allowance. Older equipment can consume more power because of part-load performance, fouling or poor controls, but age alone does not prove inefficiency. Source notes (not part of spoken script): Engineering_Analysis_and_System_Schematic(1).pdf, pages 2–3. The two 600-ton chillers and component arrangement are hypothetical. Common plant connections are aggregated. SF = supply fan; RF = return fan; P = pump group. Outdoor-air mixing/relief, valves, heating and refrigerant details are omitted from this slide. Energy!F18:F21 gives 3,043,500 kWh/year. Assumptions!C41:J43 includes a combined 150 kW water-pump allowance, not 150 kW per circuit. BAS signals shown are representative.

## Slide 3
Engineering alternatives and energy savings
Calculated HVAC electricity savings. No measured whole-building energy reduction is claimed.
3 / 7
Annual HVAC electricity (kWh)
Chart: 
| A: Existing | B: Full | C: Partial
Annual HVAC electricity | 3043500 | 1896300 | 2566500
Million kWh/year
A Existing system
Continue operating current equipment and controls.
B Full modernization
Replace chillers. Upgrade pumps, fans and controls.
Save 1,147,200 kWh/year (37.7%).
C Partial upgrade
Rebuild chillers and make selective equipment/control upgrades.
Save 477,000 kWh/year (15.7%).
Notes: Suggested timing: 55 seconds All three options serve the same assumed cooling load. Full modernization replaces both chillers and makes broader pump, fan and automation improvements. The partial option retains and rebuilds the chillers, with more selective upgrades. Both include tower refurbishment. I calculated chiller electricity by multiplying capacity, load fraction, hours and kW per ton within four load bins, then added fan, pump and tower electricity. Subtracting B and C from the baseline produces 1,147,200 and 477,000 kilowatt-hours of savings. Dividing each by 3,043,500 gives 37.7 and 15.7 percent. These are calculated HVAC electricity reductions. Schedules and performance curves need measurement or simulation before the savings can be relied upon. Source notes (not part of spoken script): Workbook: Assumptions!C33:G36 and C41:J43; Energy!F18:H22. Step 4 engineering report, pages 3–6. Load bins 25/50/75/100%, with 750/1,250/750/250 hours, totaling 1,950,000 cooling ton-hours. Whole AHU replacement is not specified. Chart uses saved annual kWh directly.

## Slide 4
Capital investment and operating savings
Planning estimates, without contractor bids. All values are USD. Cost groups reconcile to the CapEx worksheet.
4 / 7
Initial capital investment
Cost group | B: Full | C: Partial
Equipment | 2,200,000 | 565,000
Controls + monitoring | 475,000 | 265,000
Installation + enabling work | 1,500,000 | 525,000
Design, permits + training | 375,000 | 165,000
Contingency | 450,000 | 149,000
Total | 5,000,000 | 1,669,000
Year 1 pretax operating savings
Annual change | B | C
Electricity savings | 229,440 | 95,400
Maintenance / repairs | 195,000 | 110,000
Less: analytics | (25,000) | (15,000)
Net savings | 399,440 | 190,400
Illustrative electricity rate: $0.20/kWh.
Owner retains 100% of operating savings.
Notes: Suggested timing: 55 seconds The full budget totals five million dollars, compared with 1.669 million for the partial option. The table groups the existing budget line items without changing the total. These are planning allowances, not supplier quotations. I kept capital spending separate from annual operating savings. At the illustrative twenty-cent rate, electricity savings are 229,440 dollars for B and 95,400 dollars for C. Adding maintenance and repair reductions, then subtracting recurring analytics costs, gives 399,440 and 190,400 dollars of pretax savings in Year 1. The model assumes the owner retains all of those operating savings. Actual utility tariffs and lease terms would need to support that assumption. Source notes (not part of spoken script): Workbook: CapEx!C8:I25, Energy!F24:H29 and Assumptions!E22, E47:G49, E60. Equipment = chillers, tower, pumps and AHU fan/drive/damper work (rows 8–11). Controls + monitoring = rows 12+21. Installation + enabling = rows 13+15+16+19+20. Design, permits + training = rows 14+17+18. Contingency = row 24. Full total $5,000,000, partial $1,669,000. Maintenance/repair savings combine recurring categories only; future capital events remain in the cash flow model.

## Slide 5
Financial investment evaluation
Paybacks interpolate after-tax cash-flow recovery. A is the incremental baseline and still has future operating/capital costs.
5 / 7
Base-case NPV (USD millions)
Chart: 
| A: Existing | B: Full | C: Partial
Base NPV | 0 | -1754620.45 | 68530.64
Metric | B: Full | C: Partial
Dated IRR (XIRR) | −0.38% | 9.44%
Simple payback | Not within 10 years | 6.51 years
Discounted payback | Not within 10 years | 9.12 years
10-year horizon: 2027–2036
Base discount rate: 8.5%
NPV is primary: it measures discounted after-tax value in dollars.
Notes: Suggested timing: 60 seconds The valuation uses dated incremental after-tax cash flows, with the initial investment at the end of 2026 and ten operating years through 2036. NPV is the primary comparison because it accounts for the timing of cash flows and expresses value in dollars. Full modernization has a negative NPV of about 1.755 million dollars. Partial upgrade has a positive NPV of only 68,531 dollars. Its 9.44 percent IRR is only modestly above the 8.5 percent discount rate. Simple payback is 6.51 years, but discounted payback is 9.12 years. Those are interpolated after-tax recovery periods. The small positive NPV is a conditional model result, not a guaranteed profit. Source notes (not part of spoken script): Workbook: Cash Flow!D7:N8, D54:N54, D76:N76 and E89:F93; Summary!E10:F14. Exact NPVs −$1,754,620.454588824 and +$68,530.6396530481. Exact XIRRs −0.3826483% and 9.4442685%. C simple/discounted paybacks 6.509599896 / 9.118548802; year-end cash-flow crossings occur in Years 7/10. Neither B payback occurs within 10 years.

## Slide 6
Scenario analysis and investment risks
Illustrative assumption combinations, not probability forecasts. Both upgrades have negative Downside NPV.
6 / 7
10-year NPV (USD millions)
Chart: 
| Base 8.5% | Optimistic 7.0% | Downside 11.0%
B: Full | -1.7546 | -0.51431 | -3.9085
C: Partial | 0.068531 | 0.62175 | -0.83805
Percentages below scenario names are discount rates.
Assumptions that need evidence
Installed cost and scope
Achieved energy savings
Maintenance and future repairs
Electricity prices and owner savings
Tax treatment
C loses its positive base NPV with about 4.32% higher initial cost, other inputs fixed.
Notes: Suggested timing: 60 seconds The financial scenarios change several assumptions together. They are different from the A, B and C engineering alternatives. In the optimistic case, partial upgrade reaches about 622,000 dollars of NPV while full modernization remains negative. In the downside case, both upgrades are negative. These scenarios are illustrations, and their weights are subjective judgments rather than measured probabilities. The partial option has little room for error: roughly 4.32 percent higher initial cost erases its positive base NPV, with other inputs fixed. The future repair and replacement needs of the existing system are especially important because avoiding that spending is a significant benefit. Cost bids, operating measurements, lease terms and tax classification need stronger support. Source notes (not part of spoken script): Workbook: Scenarios!E8:F10 and E52; Assumptions!E61:E83. NPV pairs B/C: Base −$1,754,620.4546 / +$68,530.6397; Optimistic −$514,311.9421 / +$621,751.6997; Downside −$3,908,536.7824 / −$838,052.2225. The rate under each category is its discount-rate assumption, not the only changing input. Assumptions Validation(1).pdf, pages 8–9. C cost break-even $1,741,161 with initial related tax basis scaled consistently. Future capital event timing/scope is fixed across the standard scenarios; they do not exhaust this uncertainty.

## Slide 7
Final recommendation and conclusion
Independent student analysis. The findings support further investigation, not unconditional investment approval.
7 / 7
Advance the partial upgrade for further evaluation.
Withhold approval of either upgrade until key assumptions are supported.
Why C merits further study
Full modernization saves more electricity, but its extra $3.331 million does not produce enough discounted value within ten years.
C requires less capital, but its $68,531 base NPV leaves little margin for cost or performance errors.
Before funding
Verify installed bids and baseline repair needs. Measure performance. Confirm utility savings, lease allocation and tax treatment.
Skills demonstrated
HVAC energy calculations, Excel cash-flow modeling, NPV/XIRR, sensitivity analysis and source evaluation.
Ten years is a planning window. Excluded terminal value and later tax benefits may affect the comparison, especially for full modernization.
Notes: Suggested timing: 55 seconds My conclusion is to investigate the partial upgrade further, while withholding unconditional approval of either option. Full modernization gives the largest energy reduction, but its additional capital does not earn enough modeled value during the ten-year window. The partial option performs better financially, but its positive NPV is small and depends on assumptions that still need evidence. I would first verify installation bids and the existing equipment’s repair and replacement needs, then measure operating performance and confirm who keeps the savings. Ten years is a consistent planning period, not the equipment’s entire life. Excluded terminal value and later tax benefits may affect the comparison. This project demonstrates how I connect HVAC calculations to a defensible financial decision. Source notes (not part of spoken script): Manhattan_HVAC_Executive_Investment_Summary(1).pdf, page 1, Final Recommendation and Project Limitations. Workbook: CapEx!F25/I25 and Cash Flow!E89:F93. B−C additional initial capital $3,331,000, NPV difference −$1,823,151.0942. No terminal value or new residual-value assumption is introduced. Source uncertainty is documented in Steps 1, 3 and 4. No actual investment approval, consulting engagement or measured savings is claimed.